## Slide 1: A Preparatory Study on and the First Analysis Steps of Systematically Considering Combinations of External Events in the Design Basis and in the PSA of NPP Paks
Tamas Siklossy, Attila Bareith, Barnabas Toth
IAEA Technical Meeting on Enhancement of Methods, Approaches and Tools for the Development and Application of PSA
Online - webex, September 29 – October 2, 2019
siklossyt@nubiki.hu

## Slide 2: Content
  Introduction
  Overview of the publically available literature
  A critical review of current Hungarian practices
  Proposed technical tasks in details considering hazard combinations in the design basis and PSA
  Achievements in selection and screening of external hazard combinations
  Conclusions

## Slide 3: Introduction
  Mostly single external hazards have been considered in the definition of the design basis for the Paks NPP in Hungary
  Motivation of assessing the impact of hazard combinations on NPP safety
    Requirements laid down in Hungarian Nuclear Safety Codes and international recommendations
    Lessons learnt from the Fukusima Dai-ichi accident
    International/national R&D programs
  According to a corrective measure of the PSR of the Paks NPP in 2017: a systematic survey and assessment should be performed to:
    identify and characterize external hazard combinations
    assess the effects of hazard combinations on NPP safety:
      the adequacy of protection against hazard combinations to be included in the design basis has to be justified
      the residual risk due to beyond design basis load combinations has to be quantified
  The technical tasks and the schedule thereof had to be worked out first.

## Slide 4: Overview of the Publically Available Literature
  Hungarian regulations: NSC
  International recommendations: WENRA and IAEA
  Swedish Nuclear Inspectorate: SKI Report 02:27 (2003)
  EPRI: Identification of External Hazards for Analysis in Probabilistic Risk Assessment (Update 2015)
  Technical reports developed in the ASAMPSA_E project
  A WGRISK task and the corresponding questionnaire on external hazards PSA (2007)
  Technical articles on national assessments, e.g.:
    GRS on screening of hazard combinations
    External hazard combinations PSA for NPP Hanhikivi
  Methodological documents on multivariate distribution functions

## Slide 5: A Critical Review of Current Hungarian Practices – Design Basis
  FSAR – targeted assessment in 2002:
    no need to consider any hazard combinations in the design basis
    not a state-of-the-art analysis (simplistic, have not been updated)
  Assessments of single hazards included considerations to some potential hazard combinations
    man-made hazards – no correlation, except for meteorological conditions
    meteorology – no correlation, except for wind&snow loads on structures
    Danube contamination endangering the water intake system – combination considered in the identification of relevant event sequences
    hydrology – possible combinations of single hydrological events
    geosciences – all seismological hazards are assessed in conjunction with geotechnical, geological and tectonic conditions and hazards
    The combination among the different types of hazards was not assessed
  Site investigation and evaluation program for new NPP builds (Paks 2016-2018) – targeted assessment of hazard combinations
    the results cannot be applied directly to the existing NPP units without further investigations
    the assessment has some inherent boundaries that should be considerd, e.g. no input data derived for PSA
    need to revise and supplement quite a few analysis assumptions and evaluations

## Slide 6: A Critical Review of Current Hungarian Practices – PSA
  No dedicated PSA for hazard combinations for the Paks NPP
  PSA for single hazards includes considerations to some potential hazard combinations
    full correlation for instantaneous, daily average and weekly average air temperature and cooling water temperature
    hydraulic load assessment for the canalization system – extreme precipitation & LOOP (cooling water of diesel generators)
    potential snow induced blockage of air intake systems (wind&snow)
    fragility of the grid due to extreme temperature (all relevant grid related events that may occur)
    vulnerability of the power transmission lines to the combination of extreme wind, frost and ice formation, and high/low air temperatures
    partial correlation between earthquake and soil liquefaction

## Slide 7: Types of External Hazard Combinations
  Combination of dependent hazards – causal connection
    Consequential hazards – cause-effect relation:
      A may cause B (e.g. explosion – forest fire)
      A is a prerequisite of B (e.g. earthquake – soil liquefaction)
    Non-consequential connected hazards (correlated hazards) – common root cause (e.g. certain meteorological conditions trigger many hazardous phenomena)
  Combination of independent hazards – no causal connection
    independent events have a high occurrence frequency,
    at least one of the events is long-lasting and usually rare.

## Slide 8: Proposed Technical Tasks
PSA:
Selection of external hazard combinations
Screening of external hazard combinations
Detailed assessment of screened-in events:
  Probabilistic hazard assessment
  Plant response and fragility analysis
  Event logic modeling and risk quantification
Design basis (identification of hazard combinations and justification of plant protection):
Selection of external hazard combinations
Screening of external hazard combinations
Definition of design basis load combinations
Evaluation of plant protection and specification of protective measures

## Slide 9: Selection of External Hazard Combinations
  Development of a comprehensive list of potential single external hazards
  Screening of single hazards with respect to hazard combinations
    screening by relevance (cannot occur at the site)
    frequency based screening (Hungary: 10-7/a for an existing NPP)
  Evaluation of the dependence among the hazards
    a table („matrix”) form – cross-correlation chart
    for all the possible hazard combinations, the possible relation type has to be identified and marked with a predefined symbol
    identification of hazard combinations including 3 or more hazards:
      mapping of root causes that may trigger such combinations
      studying the dependence in rows and columns of the cross-corr. chart

## Slide 11: Selection of External Hazard Combinations – Possible relation types
↗↙ | one hazard is a prerequisite of the other hazard
↙↗ | one hazard may cause the other hazard, the impact mechanisms of the single hazards are similar or the same
↙↗ | one hazard may cause the other hazard, the impact mechanisms of the single hazards are different
 | correlated hazards, the impact mechanisms of the single hazards are similar or the same
 | correlated hazards, the impact mechanisms of the single hazards are different
 | independent hazards, the impact mechanisms of the single hazards are similar or the same
 | independent hazards, the impact mechanisms of the single hazards are different
 | mutually exclusive hazards

## Slide 12: Screening of External Hazard Combinations
  In general, the same screening criteria as for single hazards
  Relation between the impact mechanisms of the single hazards:
    similar or the same (e.g. wind & snow to structures):
      hazards affect the same SSCs amplifying one another’s effects
      resistance against the combined load has to be assessed
    different (e.g. wind & high temperature)
      hazards do not affect the same SSCs or not with the same mechanisms
  Hazard combinations specific screening criteria:
    hazards are mutually exclusive
    definition of a single hazard incorporates the other single hazard
    the impact of the hazard combination is not more severe than the effect of the more powerful hazard

## Slide 13: Screened-in Combinations of External Hazards
  storm: high wind and extreme precipitation and thunder
  snowstorm: high wind and extreme snow
  extremely high temperature conditions: extremely high air temperature and high Danube water temperature
  extremely low temperature conditions: extremely low air temperature and surface ice on the Danube (and icing and snow)
  earthquake and soil liquefaction
  earthquake and extremely high or low air temperature (independent)
  simultaneous accident in nearby industrial facilities that handle dangerous chemical substances (due to a common root cause)
  extreme meteorological conditions and handling of dangerous substances (the meteorological conditions may have a significant impact on the dispersion of dangerous substances)

## Slide 14: Probabilistic Hazard Assessment
Frequency-magnitude relationship for different magnitudes of load combinations
  combination of dependent hazards – causal connection
    consequential hazards – cause-effect relation
    correlated hazards – common root cause correlation has to be determined
      hazard curve (surface) development, e.g. multivariate extreme value theory for meteorological hazards
      current practice: hazard occurrence frequencies for predefined combinations of load intensity
  combination of independent hazards (high occurrence freq. or long-lasting event)
    occurrence frequency of event i [1/a]
    duration of event i [year]
    N duration (within a year) when both events can occur simultaneously [year]

## Slide 15: Plant Response and Fragility Analysis, Event Logic Modeling, Risk Quantification
  Plant response and fragility analysis
    which SSCs are challenged and how to characterize the vulnerability
    ideally: probability of failure for different levels of load combinations by means of fragility surfaces
    current practice: fragility for predefined combinations of load intensity
    relation between the impact mechanisms of the single hazards is decisive
  Event logic modeling and risk quantification
    approach is similar to that of the single hazards PSA
    assessment of plant transients, degradation of mitigation systems induced by hazard combination, impact on the conditions of human interactions/responses
    random SSC failures and human failure events considered too

## Slide 16: Conclusions
  As a preparatory step to systematically identify and assess the combinations of external hazards for the Paks NPP:
  the regulations and recommendations have been thorougly reviewed
  the available methodologies have been studied and evaluated
  analysis practices applied in Hungary have been examined
  a proposal has been developed for the technical tasks and the schedule thereof to identify combinations of external hazards and assess the effects of such hazards on NPP safety
  The assessment of external hazard combinations has been started in 2019 and is planned to be finished in 2022.
  Selection and screening of external hazard combinations performed

## Slide 17: Thank you for your attention!